## Standard Dwelling
Fred's Sewage System Figurer-Upper |  |  | Lineal Feet needed | two foot wide trench or equivalent |  | three foot wide trench or equivalent
WV Standard Septic Tank Soil Absorption System |  |  | gravel | 300 | ft | 200 | ft
Sizing for Single-Family Dwelling |  |  | chamber | 180 | ft | 120 | ft
Perc time: | 25 | minutes per inch | low profile chamber | 225 | ft | 150 | ft
Bedrooms: | 2 |  | 8" gravelless | 300 | ft
|  |  | 10" gravelless |  |  | 200 | ft
Estimated Gallons per day: | 280 | GPD | Number of Units needed (for laterals only - not beds)
Septic Tank Size: | 1000 | gallons | 18" wide x 5' long | 47 | units | 30 | 36" wide x 4' long
|  |  | 18" wide x 7.14' long | 34 | units | 24 | 36" wide x 5' long
Square footage needed: | Square footage needed for bed: |  | 24" wide x 4' long | 47 | units | 20 | 36" wide x 6.25' long
600 |  | 780 | 24" wide x 5' long | 36 | units | 38 | 36" wide (low profile) x 4' long
|  |  | 24" wide x 7.14' long | 25 | units | 30 | 36" wide (low profile) x 5' long
|  |  | BEDS Eljen GSF | 16 | modules (minimum)
|  |  | For a chamber bed, | enter units from above |  | 48 | units
|  |  |  | Units for bed |  | 63 | units

## Establishment not dwelling
Fred's Figurer-Upper June 2011 |  |  | Lineal Feet needed | two foot wide trench or equivalent |  | three foot wide trench or equivalent
WV Single Absorption System Sizing for Establishment |  |  | gravel | 875 | ft | 583.3333 | ft
Other Than Single-Family Dwelling |  |  | chamber | 525 | ft | 350 | ft
Perc time: | 25 | minutes per inch | low profile chamber | 656.25 | ft | 437.5 | ft
Number of people: | 100 |  | 8" gravelless | 875 | ft
Estimate GPD/person: | 7 | GPD | 10" gravelless |  |  | 583.3333 | ft
Number of Units needed (for laterals only - not beds)
Gallons per day: | 700 | GPD | 18" wide x 5' long | 135 | units | 88 | 36" wide x 4' long
Septic tank size: | 1050 | Gallons | 18" wide x 7.14' long | 98 | units | 70 | 36" wide x 5' long
|  |  | 24" wide x 4' long | 135 | units | 57 | 36" wide x 6.25' long
Square footage needed: | Square footage needed for bed: |  | 24" wide x 5' long | 103 | units | 110 | 36" wide (low profile) x 4' long
1750 |  | 2275 | 24" wide x 7.14' long | 73 | units | 88 | 36" wide (low profile) x 5' long
|  |  | BEDS Eljen GSF | 47 | modules (minimum)
|  |  | For a chamber bed, | enter units from above |  | 48 | units
|  |  |  | Units for bed |  | 63 | units

## LPP Sizing Standard
WV LPP - Low Pressure Pipe Sizing July 2011 |  |  | Gallons per day: | 750 | GPD | supply line volume | 5.67
Perculation time: | 90 | minutes per inch | Size of septic tank: | 1250 | gallons | lateral volume | 16.2
Bedrooms: | 5 |  | Size of pumping tank: | 1500 | gallons
Spacing between laterals (lines): | 5 | feet | Maximum Loading Rate: | 0.1 | gpd/ft2 |  | c= | 130 | where C is a Hazen-Williams roughness coefficient for PVC pipe
Dosing hole spacing: | 5 | feet | Total Area Needed: | 7500 | ft2 |  | q= | 1 | where q is the flow in gpm
Dosing hole size: | 5 | thirty-seconds | Number of dosing holes: | 300 | holes |  | d= | 1 | where d is the inside diameter of the pipe
Pressure head: | 3 | feet | Lineal Feet Needed: | 1500 | feet
Elevation head: | 5 | feet | Gravel Needed to fill a six-inch | 22.5 | yards or |  | f= | 0.12813 | where f is the friction loss in ft per 100 ft of pipe
Dosing Pipe Diameter: | 2 | inch | wide trench six inches deep: | 28.5 | tons
Dosing frequency: | 2 | per day | Flow rate per hole: | 0.5 | GPM
2" SCH-40 Supply line length: | 35 | feet | Minimum volume per dose: | 610.335 | gallons |  | based upon Hazen-Williams formula shown below
|  |  | Total flow rate: | 150 | GPM
|  |  | Total flow rate with 1/4" siphon-breaker hole: | 152 | GPM |  | f = 0.2083 (100/c)^1.852 q^ 1.852 / d^4.8655
Buy a pump that can exceed | 152 | GPM at | Friction head: | 0.924 | feet
a total head of | 8.924 | FEET. | Total head: | 8.924 | feet

## LPP Sizing Other
WV LPP - For other than dwelling Sept 2011 |  |  | Gallons per day: | 280 | GPD
Perculation time: | 90 | minutes per inch | Size of septic tank: | 1000 | gallons
Gallons per Day: | 280 |  | Size of pumping tank: | 560 | gallons
Spacing between laterals (lines): | 5 | feet | Maximum Loading Rate: | 0.1 | gpd/ft2
Dosing hole spacing: | 5 | feet | Total Area Needed: | 2800 | ft2
Dosing hole size: | 5 | thirty-seconds | Number of dosing holes: | 112 | holes
Pressure head: | 3 | feet | Lineal Feet Needed: | 560 | feet
Elevation head: | 5 | feet | Gravel Needed to fill a six-inch | 8.4 | yards or
Dosing Pipe Diameter: | 2 | inch | wide trench six inches deep: | 10.64 | tons
Dosing frequency: | 2 | per day | Flow rate per hole: | 0.5 | GPM
2" SCH-40 Supply line length: | 35 | feet | Minimum volume per dose: | 0 | gallons
|  |  | Total flow rate: | 56 | GPM
|  |  | Total flow rate with 1/4" siphon-breaker hole: | 58 | GPM
Buy a pump that can exceed | 58 | GPM at | Friction head: | 0.924 | feet
a total head of | 8.924 | FEET. | Total head: | 8.924 | feet

## Sloopie Calculator
Sloopie Calculator - FRB March 2006
Enter degrees: | 30
% Slope is: | 57.735
Enter slope %: | 30
Degrees is: | 16.6992
Written for Jonathan Graziani
ought x ought = ought
ought x one = ought
ought x two = ought

## Tank Capacity
Septic Tank Capacity Calculator
| Interior Length in inches: | 72
| Interior width in inches: | 60
| Depth from bottom of the tank to the bottom of the outlet in inches: | 50
| Capacity in Gallons: | 935.125
Dosing depth Calculator Method #1
Depth from bottom of the tank to the bottom
| of the outlet in inches: | 48 | inches
| Capacity of tank: | 1000 | gallons
| Volume per dose: | 170 | gallons
| Depth of dose: | 8.16 | inches
Dosing depth Calculator Method #2
| Interior length of tank: | 72 | inches
| Interior width of tank: | 48 | inches
| Volume per dose: | 170 | gallons
| Depth of dose: | 11.3621 | inches

## Chamber Specs
Units Approved For Use in West Virginia
| 4' | 5' | 6.25' | 7.14' | 8.33'
18" | N/A | ADS Arc 18 | N/A | ADS Bio 2 | N/A
24" | Infiltrator (Quick4 EQ24, Quick4 Plus EQ 24) | ADS Arc 24 | N/A | ADS Bio 3 | Infiltrator Equilizer 36
36" | Infiltrator (Quick4 EQ36, Quick4 Plus EQ 36) | ADS Arc 36 | ADS BioDiffuser 11" Standard | N/A | N/A | For chambers not listed, enter the nominal width and length below for square footage equivalency per unit
18" LP | N/A | N/A | N/A | N/A | N/A | WIDTH | 3 | feet
24" LP | N/A | N/A | N/A | N/A | N/A | LENGTH | 4.5 | feet
36" LP | Infiltrator (Quick4 Standard, Quick4 Plus Standard) | ADS Arc 36 LP | N/A | N/A | N/A | EQUIVALENCY | 23 | square feet
[6 empty] | Low Profile Equivalency | 18 | square feet
Square footage Equivalency per unit (rounded to one decimal)
| 4 | 5 | 6.25 | 7.14 | 8.33 | When calculating how many
18" | 10.02 | 12.525 | 15.6562 | 17.8857 | 20.8666 | units you will need, always
24" | 13.36 | 16.7 | 20.875 | 23.8476 | 27.8222 | round UP. If you show 17.2 units
36" | 20.04 | 25 | 31.3125 | 35.7714 | 41.7333 | needed, then use 18 units.
18" LP | 7.98 | 9.975 | 12.4688 | 14.2443 | 16.6184
24" LP | 10.64 | 13.3 | 16.625 | 18.9924 | 22.1578
36" LP | 15.96 | 19.95 | 24.9375 | 28.4886 | 33.2367